# 7123AS	AQUATHERM® FLEXI HOT & COLD WATER SYSTEM

## 1.	GENERAL

If you have pre-customised this work section using the "questions and answers" provided as part of the downloading process, it may be necessary to amend some clauses to suit the final project-specific version.

The section must still be checked and customised to suit the project being specified, by removing any other irrelevant details and adding project-specific details and selections.

This section relates to aquatherm® flexi potable water systems from the network utility supply authority water main to designated points and appliances, distributing piped hot water to appliances, and the installation of tap ware.

Modify or extend the above description to suit the project being specified.

### 1.1	RELATED WORK

Refer to 7151 SANITARY FIXTURES, TAPWARE & ACCESSORIES for tapware selections.

Include cross references to other sections where these contain related work.

Documents

### 1.2	DOCUMENTS

Refer to the general section 1233 REFERENCED DOCUMENTS.  The following documents are specifically referred to in this section:

NZBC C/AS1-AS7	Protection from fire

NZBC G4/AS1	Ventilation

NZBC G12/AS1	Water supplies

NZBC H1/AS1	Energy efficiency

AS/NZS 2845.1	Water supply - Backflow prevention devices - Materials, design, and performance requirements

AS 2845.3	Water supply - Backflow prevention devices - Field testing and maintenance

AS/NZS 3500.5	Plumbing and drainage - Housing installations

AS 3688	Water supply - Metallic fittings and end connections

NZS 4305	Energy efficiency - Domestic type hot water systems

NZS 4602	Low pressure copper thermal storage electric water heaters

NZS 4607	Installation of thermal storage electric water heaters: valve vented Systems

NZS 4617	Tempering (3-port mixing) valves

AS/NZS 5601.1: 2010	Gas installations - general installations

ISO 22391-2	Plastic piping systems for hot and cold water installations - polyethylene of raised temperature PERT

Gas (Safety and Measurement) Regulations 2010

Plumbers, Gasfitters and Drainlayers Act 2006

Delete from the DOCUMENTS clause any document not cited.  List any additional cited documents.

The following are related documents and if referred to in the work section need to be added to the list of DOCUMENTS.

NZS 1170.5	        Structural design actions - Earthquake actions - New Zealand

AS/NZS 3500.1	Plumbing and drainage - Water services

AS/NZS 3500.4	Plumbing and drainage - Heated water services

NZS 4219	        Seismic performance of engineering systems in buildings

BRANZ BU 364	Preventing noise in plumbing installations

### 1.3	MANUFACTURER'S DOCUMENTS

Manufacturer's and supplier's documents relating to work in this section are:

aquatherm® flexi technical manual

BRANZ Appraisal 708 - aquatherm® flexi Piping System

Manufacturer/supplier contact details:

Company:	aquatherm NZ Ltd

Web:	www.aquatherm.co.nz

Email:	sales@aquatherm.co.nz

Telephone:	0-9-570 7204

It is important to ensure that all personnel on site have access to accurate, up to date technical information on the many products, materials and equipment used on a project.  In most cases individual products are not used in isolation, but form part of a building process.  Also a particular manufacturer's and/or supplier's requirements for handling, storage, preparation, installation, finishing and protection of their product can vary from what might be considered the norm.  Access to technical information can help overcome this potential problem.

Warranties

### 1.4	WARRANTY - MANUFACTURER/SUPPLIER

Provide an aquatherm® 50 year warranty of service life

10 years:	For third party warranty for property and bodily damage (refer to Aquatherm NZ Ltd for details)

-	Provide this warranty on the manufacturer/supplier standard form.

-	Commence the warranty from the date of completion of system testing.

Refer to the general section 1237 WARRANTIES for additional requirements.

Modify or expand the clause to suit project or manufacturer/supplier requirements, options include:

-	Change the standard form to be used (check with the manufacturer/supplier, use the general section 1237WA WARRANTY AGREEMENT if required)

-	Commence the warranty from the date of purchase (check with the manufacturer/supplier)

### 1.5	WARRANTY - INSTALLER

Provide an installer warranty:

2 years:	For work under normal environment and use conditions and failure of execution

-	Provide this warranty on the installer's standard form.

-	Commence the warranty from the date of practical completion of the contract works.

Refer to the general section 1237 WARRANTIES for additional requirements.

Modify or expand the clause to suit project or installer requirements, options include:

-	Change the standard form to be used (check with the installer, use the general section 1237WA WARRANTY AGREEMENT if required)

-	Commence the warranty from the date of installation (check with the installer)

Requirements

### 1.6	NO SUBSTITUTIONS

Substitutions are not permitted to any specified aquatherm® flexi or associated products, components or accessories.

### 1.7	QUALIFICATIONS

Plumbers to be certified aquatherm® installers, familiar with the materials and the techniques specified.  Carry out all work under the direct supervision of a certifying plumber under the Plumbers, Gasfitters and Drainlayers Act 2006.

Refer to www.aquatherm.co.nz for a list of certified installers.

### 1.8	INFORMATION FOR MAINTENANCE MANUAL

Supply maintenance manual information to requirements set out in the 1239 OPERATION & MAINTENANCE section.

Check the general section 1239 OPERATION & MAINTENANCE or for Masterspec Basic 1234 DOCUMENTATION, and modify requirements if those set out are too onerous or too basic for the project in hand.  If not using 1239 OPERATION & MAINTENANCE section change to 1234 DOCUMENTATION.

Confirm when and where the information is to be supplied and in what numbers.

Performance

### 1.9	DURABILITY

aquatherm® flexi meets the 50 year durability requirements of NZBC B2/AS1 for pipes cast into concrete to Aquatherm requirements.

### 1.10	TESTING

Confirm the timing before carrying out any tests.  Supply potable water and the apparatus needed.  Ensure that any connected tapware is isolated before commencing testing.  Test to aquatherm® flexi testing procedures as applicable.  Provide completed test records in the aquatherm® New Zealand Products Catalogue standard form.

### 1.11	GAS CERTIFICATE OF COMPLIANCE

Provide a Certificate of Compliance (CoC) as required by the Gas (Safety and Measurement) Regulations 2010 to the owner, and when required provide a copy to the energy supplier before connection.

Note that a gas-powered heating/ventilating system may need to be certified by an independently qualified person (IQP).

### 1.12	GAS SAFETY CERTIFICATION

Provide a Gas Safety Certificate (GSC) as required by the Gas (Safety and Measurement) Regulations 2010 and provide a copy to the owner and when required the BCA.  To be provided at completion of the work, prior to Practical Completion.

Note that a gas-powered heating/ventilating system may need to be certified by an independently qualified person (IQP).  A Certificate of Compliance (CoC) would be required for the Code of Compliance to be signed off by the BCA.

### 1.13	GAS APPLIANCE COMPLIANCE

Supplier to provide Supplier Declaration of Compliance (SDoC) in accordance with the requirements of the Gas (Safety and Measurement) Regulations 2010.

This provision, which becomes mandatory on 01 July 2013, requires an importer or New Zealand manufacturer to provide a SDoC prior to supplying the gas appliance.

## 2.	PRODUCTS

Materials

### 2.1	AQUATHERM FLEXI POLYETHYLENE RT WATER PIPE

aquatherm® flexi pipes to ISO 22391-2 complete with sliding sleeves to AS 3688 and accessories brand-matched.

### 2.2	WATER METER

To the requirements of the network utility operator.

### 2.3	VALVES

Pressure reducing or limiting valve, filter, non-return valve, cold water expansion valve, pressure relief valve, pressure relief valve and isolating valves to NZBC G12/AS1.

### 2.4	TEMPERING VALVE

Tempering valve to NZS 4617 to NZBC G12/AS1.

### 2.5	BACKFLOW PREVENTION DEVICES

Provide backflow prevention devices to AS/NZS 2845.1 where it is possible for water or contaminants to backflow into potable water supply.  Refer to NZBC G12/AS1, 3.4 Backflow protection, and NZBC G12/AS1, table 2, Selection of Backflow Prevention.

### 2.6	HEADER TANKS

Pre-formed black polyethylene or stainless steel tank, complete with access opening and lid and overflow tray.

### 2.7	INSULATION

Pre-formed pipe sections complete with bends and fittings, with fixing tape to the manufacturer's requirements.

Materials available are fibreglass, polyurethane, rock fibre and flexible foam.  Finishes - plain, calico and aluminium foil.

Materials - hot water heating appliances

Modify the following selections to suit requirements.  Add instantaneous electric water heaters where appropriate.

### 2.8	ELECTRIC HOT WATER CYLINDER, MAINS PRESSURE

To NZS 4305, ceramic-coated steel thermal storage cylinder, insulated and complete with required fittings.

Change to plural where appropriate.

### 2.9	ELECTRIC HOT WATER CYLINDER, LOW PRESSURE

To NZS 4305 and NZS 4602 copper thermal storage cylinder, insulated and complete with pressure reducing valve and required fittings.

Change to plural where appropriate.

### 2.10	ELECTRIC HOT WATER CYLINDER, UNDER SINK, LOW PRESSURE

To NZS 4305 and NZS 4602 copper thermal storage cylinder, insulated and complete with required fittings.

Change to plural where appropriate.

### 2.11	ELECTRIC BOILING CYLINDER, WALL MOUNTED

To NZS 4305 wall-mounted boiling water heater in pre-finished cabinet, complete with tap draw off.

Change to plural where appropriate.  Modify where the boiling cylinder is concealed.

### 2.12	GAS HOT WATER HEATER, STORAGE TYPE

Insulated cylinder to NZS 4305 with an integral gas burner and flue.

Change to plural where appropriate.  Both externally and internally-mounted cylinders are available, for either natural gas or LPG.

### 2.13	GAS HOT WATER HEATER, CONTINUOUS FLOW TYPE

Continuous flow unit with an integral gas burner and flue to NZS 4305.

Change to plural where appropriate.  Both externally and internally-mounted cylinders are available, for either natural gas or LPG.

Remote digital controllers are available for these units.  Refer to the manufacturer for details and list in SELECTIONS.

Components

### 2.14	PIPE CLAMPS

aquatherm® proprietary pipe clamps and clips.

### 2.15	VALVES

aquatherm® proprietary valves and ball cocks as selected and required.

## 3.	EXECUTION

Conditions

### 3.1	HANDLE AND STORE

Handle and store pipes, fittings and accessories to avoid damage.  Store on site, under cover, out of direct sunlight, on a clean level area, stacked to eliminate movement and away from work in progress in accordance with the aquatherm® flexi technical manual.

### 3.2	CORE HOLES AND SLEEVES

Review location and fit core holes and sleeves as needed throughout the structure in conjunction with the boxing, reinforcing and placing of concrete.  Strip core holes and make good after installation of pipework.

### 3.3	FASTENING TECHNIQUE

Fix pipework using aquatherm® proprietary pipe brackets, spacing in accordance with the aquatherm® flexi technical manual.  Ensure brackets are set out as fixed or sliding points in accordance with the aquatherm® flexi technical manual.

### 3.4	CONCEAL

Conceal pipework within the fabric of the building unless detailed otherwise.  Satin finish chrome plate exposed work, complete with matching ferrule at the surface penetration.

### 3.5	IN CONCRETE INSTALLATION

Install directly in concrete in accordance with aquatherm® flexi installation procedures.

### 3.6	IN GROUND INSTALLATION

Install to AS/NZS 3500.5, clause 2.13.4 Under concrete slabs.

### 3.7	THERMAL MOVEMENT

Accommodate movement in pipes resulting from temperature change by the layout of the pipe runs, by expansion joints and by sleeving through penetrations.  Install pipework in accordance with theaquatherm® flexi technical manual.

### 3.8	PIPE SIZE

Flow rates to each outlet to be no less than those given in NZBC G12/AS1, table 3, Acceptable flow rates to sanitary fixtures, with pipe size as determined in NZBC G12/AS1, table 4, Tempering valve and nominal pipe diameters and in accordance with the aquatherm® flexi technical manual.

Basic information can be obtained from the aquatherm® technical manual.

Application - jointing

### 3.9	AQUATHERM FLEXI POLYETHYLENE RT WATER SUPPLY

Size the piping layout to eliminate loss of pressure at any point by simultaneous draw-off.  Run pipes complete with all fittings, support and fixing, sliding sleeve joins and install to manufacturers specifications, all to NZBC G12/AS1.  Conceal pipework and pressure test before the wall linings are fixed.

Application - distribution systems

### 3.10	WATER SUPPLY CONNECTION

Arrange with the network utility operator for a connection to the water main and from there through a water meter and gate valve.  Provide back flow prevention to NZBC G12/AS1.

Modify this clause to suit the project's water supply requirements regarding form, pipe material (metal or plastic), configuration and high hazard situations.

### 3.11	COLD WATER INSTALLATION

From connection point, size the runs and branches to deliver the acceptable flow rate to NZBC G12/AS1, table 3, Acceptable flow rates to sanitary fixtures at each outlet.  Allow for the expected concurrent use of adjoining fixtures.  Lay out pipes in straight runs with support spacing to NZBC G12/AS1, table 7, Water supply pipework support spacing firmly fixed and buffered to eliminate noise and hammer, with preformed tee-connection take-offs and branches, with bends to aquatherm® flexi requirements, complete with necessary valves and fittings.

Refer to aquatherm® flexi technical manual.

### 3.12	MAIN ISOLATING VALVE

Install a proprietary isolating ball cock in an accessible position at the point of entry to the building.

### 3.13	IN LINE FILTER

Install an in line filter immediately adjacent to the isolating valve in an accessible position to allow for easy cleaning.

### 3.14	HOT WATER PIPEWORK

Use a take-off spigot to give separate branches to each fitting, lay out pipes with support spacing to NZBC G12/AS1, table 7 Water supply pipework support spacing.  Fix firmly and buffer to eliminate noise and hammer, with preformed tee-connection take-offs and branches, with bends to aquatherm® flexi requirements, complete with all necessary valves and fittings.

### 3.15	INSULATION

Lag all pipes with insulation to the manufacturer's requirements.  Refer to SELECTIONS for type.

Refer to NZBC G12/AS1 for areas where insulation is required.

Installation - hot water systems

Modify this section to more closely describe the required installation, which might include mains or low pressure and/or cylinders installed in series.

### 3.16	HOT WATER CYLINDER INSTALLATION GENERALLY

Install hot water cylinders complete to the manufacturer's requirements and to NZBC G12/AS1, 6. 11, Water heater installation.  Valve-vented systems to NZS 4607.

### 3.17	SEISMIC RESTRAINTS - GAS WATER HEATING APPLIANCES

Gas appliances to be restrained to manufacturer's requirements, AS/NZS 5601.1 and NZBC C/AS1-AS7, 7.2 Gas-burning Appliances.

NOTE:
Gas appliances restrained to NZBC C/AS1-AS7, 7.2, results in loadings to NZS 1170.5 and design to NZS 4219, which is quite complex.  Check the appliance manufacturer's restraint details comply, or use Engineers details, as it is unlikely the plumber will be able to provide other details.

### 3.18	SEISMIC RESTRAINTS - NON-GAS WATER HEATING APPLIANCES

Non-gas (electric, wet-back, solar etc) water heating appliances to be restrained to manufacturer's requirements and NZBC G12/AS1, 6.11, Water Heater Installation.

NOTE:
For non-gas appliances  NZBC G12/AS1 provides restraint options, one option for storage cylinders of up to 360 litres, is NZBC G12/AS1, figure 14, which is an easily understood solution.

### 3.19	INSTALL HOT WATER PIPE INSULATION

Insulate all hot water pipes to NZBC H1/AS1, AS/NZS 3500.5, 3.33 Water and Energy Efficiency, and to the insulation manufacturer's instructions.  Cut insulation sections tight between timber framing and tight between the webs of steel studs.

### 3.20	INSTALL ELECTRIC HOT WATER CYLINDERS AND BOILING CYLINDERS

Install where shown complete with all the necessary fittings to the cylinder manufacturer's requirements and in accordance with NZBC G12/AS1: 6.11.  Valve-vented systems to NZS 4607.

### 3.21	INSTALL LOW PRESSURE UNDER-SINK HOT WATER CYLINDER

Install hot water cylinders complete to the manufacturer's requirements and to NZBC G12/AS1, 6.11 Water heater installation.  Connect to sink tap.

Modify this or the following clause to suit an under-sink boiling unit.

### 3.22	INSTALL WALL-MOUNTED BOILING CYLINDER

Install to the cylinder manufacturer's stated requirements.  Locate where shown.

### 3.23	INSTALL GAS HOT WATER HEATER, STORAGE TYPE

Install complete with the necessary fittings to the manufacturer's requirements and in accordance with NZBC G12/AS1, 6. 11 Water heater installation. Install flue in accordance with the manufacturer's details and requirements and, AS/NZS 5601.1 (for internal or external appliances) or NZBC G4/AS1 (internal appliances).  Also refer to section 7221 GAS APPLIANCES for installation of gas appliances.

Coordinate installation of gas appliances with appropriate gas sections, 7211 GAS SYSTEM UTILITY NETWORK or 7212 GAS SYSTEM LPG CYLINDERS.

Add further detail on the necessary flue installation and ventilation around the unit itself, especially when the unit is mounted inside.

### 3.24	INSTALL GAS HOT WATER HEATER, CONTINUOUS FLOW TYPE

Install complete with the necessary fittings to the manufacturer's requirements and in accordance with NZBC G12/AS1, 6. 11, Water heater installation.  Install flue in accordance with the manufacturer's details and requirements and, AS/NZS 5601.1 (for internal or external appliances) or NZBC G4/AS1 (internal appliances).  Also refer to section 7221 GAS APPLIANCES for installation of gas appliances.

Coordinate installation of gas appliances with appropriate gas sections, 7211 GAS SYSTEM UTILITY NETWORK or 7212 GAS SYSTEM LPG CYLINDERS.

Add further detail on the necessary flue installation and ventilation around the unit itself, especially when the unit is mounted inside.

### 3.25	INSTALL HOT WATER CYLINDER OVERFLOW TRAY

Install drained overflow tray to hot water cylinder to NZBC G12/AS1.

### 3.26	INSTALL TEMPERING VALVE

Install 1 metre minimum from outlet of hot water cylinder and to manufacturer's instructions.  Install copper pipework for 1 metre minimum downstream of tempering valve prior to connection of non-metallic pipework.

Installation - tapware

### 3.27	INSTALLING APPLIANCE ISOLATING VALVES - CONCEALED

Install isolating valves for appliances in accessible positions.  Locate in adjacent cupboards and position to allow for easy connection and operation.

This applies to dishwashers, washing machines and refrigerators with icemakers.

### 3.28	INSTALLING TAPWARE

Install to manufacturer's requirements.

Modify this clause to more closely reflect project requirements.

### 3.29	INSTALLING BACKFLOW PREVENTION DEVICE

Provide and install backflow prevention device as near as practicable to the potential source of contamination, and in an accessible position for maintenance and testing to AS 2845.3 or NZ Backflow Testing Standard.

Completion

### 3.30	FLUSH OUT PIPEWORK

Flush out pipework.  Remove all filters, clean and reassemble.

### 3.31	REPLACE

Replace damaged or marked elements.

### 3.32	LEAVE

Leave work to the standard required by following procedures.

### 3.33	REMOVE

Remove debris, unused materials and elements from the site.

## 4.	SELECTIONS

For further details on selections go to www.aquatherm.co.nz.

Substitutions are not permitted to the following, unless stated otherwise.

SELECTIONS is for providing details of the actual selections to be included in the contract works including model numbers, colours and other information necessary to ensure that the correct materials are supplied and installed.

Water main

### 4.1	AQUATHERM FLEXI POLYBUTYLENE WATER MAIN

Size:	~mm outside diameter aquatherm®flexi

Pipework options:	16mm, 20mm, 25mm

Pipework

### 4.2	AQUATHERM FLEXI PIPE WORK

Branch off take:	16mm outside diameter aquatherm® flexi

Branch main:	20mm outside diameter aquatherm® flexi

Main:	25mm outside diameter aquatherm® green pipe

### 4.3	HOT WATER RING MAIN AQUATHERM GREEN PIPE

Pipework:	~mm outside diameter aquatherm® green pipe

Insulation:	~

Pump:	~

Pipework options:	16mm, 20mm, 25mm

Specify ring main systems in larger houses where a quality delivery system is required.

### 4.4	INSULATION

Brand:	~

Material:	~

Wall thickness:	~

Finish:	~

Materials available are fibreglass, polyurethane, rock fibre.  Finishes - plain, calico and aluminium foil.

Hot-water systems

### 4.5	ELECTRIC HOT WATER CYLINDER, MAINS PRESSURE

Brand:	 ~

Model/size:	~

### 4.6	ELECTRIC HOT WATER CYLINDER, LOW PRESSURE

Brand:	 ~

Model/size:	~

### 4.7	ELECTRIC HOT WATER CYLINDER, UNDER-SINK, LOW PRESSURE

Brand:	 ~

Model/size:	~

### 4.8	ELECTRIC BOILING CYLINDER, WALL MOUNTED

Brand:	 ~

Capacity:	~litres

### 4.9	GAS HOT WATER HEATER, STORAGE TYPE

Brand:	 ~

Model number and capacity:	~

Gas type:	~

Both externally and internally-mounted cylinders are available, for either natural gas or LPG supply.

Gas type:	natural gas, LPG

### 4.10	GAS HOT WATER HEATER, CONTINUOUS FLOW TYPE

Brand:	 ~

Model size:	~

Remote controller:	~

Gas type:	~

Remote digital controllers are an optional extra and must be specifically specified. Types include a Compact controller, Shower proof control (for wet areas) and a Deluxe bath controller. Refer to the manufacturer for full details.

Gas type:	natural gas, LPG

Valves and accessories

### 4.11	MAIN ISOLATING VALVE

Location:	~

Brand/type:	aquatherm® ball valve

Suggested location is in a readily accessible position in a plant room or garage.

### 4.12	IN LINE FILTER

Location:	~

Brand/type:	~

Suggested location is adjacent to the main isolating valve and positioned for easy access for cleaning.

### 4.13	FLOOR/ZONE ISOLATING VALVES

Location:	~

Brand/type:	aquatherm® flexi ball valve

Suggested location is in an accessible position such as service or store rooms.

### 4.14	APPLIANCE ISOLATING VALVES - CONCEALED

Appliance:	~

Brand/type:	aquatherm® flexi ball valve or concealed valves to suit application

Suggested appliances include dishwashers, washing machines and refrigerators with icemakers.

### 4.15	APPLIANCE ISOLATING VALVES - EXPOSED

Appliance:	Washing machine

Brand/type:	Refer to tapware selections

Suggested appliances include dishwashers and washing machines.

### 4.16	TEMPERING VALVE

Location:	~

Brand/type:	~